# Conditions:

Duct OD = 77mm

Duct ID = 75mm

Duct Length = 5m

Air Flow rate = 800 l/min

Air temperature entering duct = 200°C

Ambient temperature = 20°C

Material = 321 Stainless Steel

1. The forced convection heat transfer coefficient between the air and the inside surface of the duct
2. The equivalent heat transfer coefficient across the wall of the duct
3. The natural convection heat transfer coefficient between the outside wall of the duct and the outside air at 20°C.

Item 1 can be determined from the heat transfer correlation presented in Fig. 14.3-2 of Transport Phenomena. This expresses the Nusselt number (dimensionless heat transfer coefficient) as a function of the Reynolds number for the flow and the Prantdl number of the air. From the ideal gas law, the density of the inlet air is

### Density of inlet air:

ρ = air density (kg/m3)			M = Molar mass (dry air)

P = absolute pressure (Pa)		R = Specific gas constant (K J/mol K)

T = Absolute temperature (K)

ρ=PMRT=(101325)(0.029)(8.314)(473)

=0.747kgm3

### Mass flow rate:

Q = Volumetric flow rate

m˙= ρQ=0.7470.8=0.598 kg/min=0.00996 kg/sec

### Viscosity of air at 200°C:

μ=2.58×10-5 kgm.sec

### Reynolds Number:

Re=ρvDμ=4(˙m)πDμ=(4)(0.00996)(3.14159)(0.075)(2.58×10-5)=6553

6553>4000 which indicates that the flow Is turbulent

From the heat transfer = correlation (Fig 12.3-2 of transport Phenomena) see appendix A. At this Reynolds number the Nusselt number is given by

Nu=hDk=0.004(Re)(Pr)13=(0.004)(6553)(0.7)13=23.27

Thermal conductivity of air at 200°C is 0.0382 Wm.C

Initial internal heat transfer coefficient given by:

hinside= kDNu= 0.03820.07523.27=11.85 Wm2.C

For conductivity through the wall of the ducting material, the heat transfer coefficient Is equal to the thermal conductivity ÷ thickness of the wall. Thermal conductivity of the 321 Stainless Steel = 16.1 W/m.C therefore:

hwall= 16.10.001=16100Wm2.C

For natural convection heat transfer outside the ducting, Bird et al (transport phenomena) gives the equation for the outside Nusselt Number from a ducting with an atmospheric element on the outside.

Nuoutside =0.365(Gr)0.25

Where Gr = Grasof number:

Gr= gβTW-T0D3v2

g is gravitational acceleration due to Earth

β is the coefficient of thermal expansion (equal to approximately 1/T for ideal gases)

Tw is the surface temperature

T0 is the atmospheric temperature

D is the diameter

ν is the kinematic viscosity.

Where β is the coefficient of volumetric thermal expansion. The Nusselt number is going to be a function of the wall temperature itself, so the natural convection calculation is also going to be iterative. The higher the Nusselt number for the outside natural convection could be is if the outside wall temperature were equal to the inlet gas temperature, such that:

Gr= gβTW-T0D3v2

Gr=(9.81)(1/473)(180)(0.075)3(2.58×10-5/0.747)2=1.12×106

NUoutside,max=0.365(1.12×106)0.25=11.87

Therefore the max possible value of the outside heat transfer coefficient is:

houtside max=11.87kD=(11.87)(0.0382)0.075=6.04 Wm2.C

Transport phenomena table 14.1-1 (see appendix B) proves that this value is consistent within the expected range.

Total heat transfer coefficient:

1U=1hinside+1hwall+1houtside

1Umax=111.85+116100+16.04=0.25

Solution for the differential heat balance equation for the ducting gives the following equation for the exit temperature of the air from the ducting

Texit=20+(200-20)exp⁡(-UAm˙Cp)

where A is the total heat transfer area in the duct πDL

Next, calculating the upper bound to the estimate of  UAm˙Cp in the above equation:

UmaxAm˙Cp=0.394(1.178)(0.00996)(3.5)(8.314)(100029)=0.04

Sub into equation for exit temperature gives a lower limit to what the exit temperature can be

Texit,min=20+200-20exp-0.04=192.94°c

# Appendices: