## Sheet1
| d1 | 7.98
| d2 | 6.06
|  |  | 3.99 | 3.03
8" inlet and outlet N=400 |  | P1 |  |  | 6" flow vel. | 8" flow vel | pressure change due to velocity change |  |  | pressure drop from online calc (6" pipe 34 ft Length) |  |  |  | 6" flow vel. | 8" flow vel | pressure drop in reducer | [5 empty] | 8" inlet and outlet using affinity law N=410 |  | P1 | 6" flow vel. | 8" flow vel | pressure change due to velocity change |  |  |  | 8" inlet and outlet using affinity law N=415 |  | P1 | 6" flow vel. | 8" flow vel | pressure change due to velocity change
q (gpm) | H (ft) | H (in PSI) | A1 | A2 | ft/sec | ft/sec | dp | P2 | H (new) |  | P2 | H new | q (gpm) | ft/sec | ft/sec | Dp | [5 empty] | q (gpm) | H (ft) | H (in PSI) | ft/sec | ft/sec | dp | P2 | H (new) |  | q (gpm) | H (ft) | H (in PSI) | ft/sec | ft/sec | dp | P2 | H (new)
[5 empty] | V2 | V1 | psi | Psi | ft | dp | psi | ft |  | V2 | V1 | psi | [8 empty] | V2 | V1 | psi | Psi | ft |  |  |  |  | V2 | V1 | psi | Psi | ft
300 | 31 | 13.454 |  |  | 3.3363 | 1.924 | 0.04978 | 13.4042 | 30.8853 | 0.08 | 13.374 | 30.8157 | 380 | 4.2259 | 2.437 | 0.01 | 0.02 | 0.06 | 0.10978 | 13.3442 | 30.7471 | 307.5 | 32.5694 | 14.1351 | 3.4197 | 1.9721 | 0.0523 | 14.0828 | 32.4489 | 9.8904 | 311.25 | 33.3686 | 14.482 | 3.4614 | 1.9961 | 0.053583 | 14.4284 | 33.2451
400 | 30.2 | 13.1068 | 50.0145 | 28.8426 | 4.4484 | 2.5653 | 0.088498 | 13.0183 | 29.9961 | 0.14 | 12.9668 | 29.8774 | 450 | 5.0044 | 2.886 | 0.01 | 0.04 | 0.1 | 0.1885 | 12.9183 | 29.7657 | 410 | 31.7289 | 13.7703 | 4.5596 | 2.6294 | 0.092978 | 13.6774 | 31.5146 | 9.6057 | 415 | 32.5075 | 14.1082 | 4.6152 | 2.6615 | 0.095259 | 14.013 | 32.288
430 | 30 | 13.02 |  |  | 4.782 | 2.7577 | 0.10227 | 12.9177 | 29.7644 | 0.16 | 12.86 | 29.6313 | 500 | 5.5605 | 3.2066 | 0.01 | 0.04 | 0.12 | 0.22227 | 12.7977 | 29.4879 | 440.75 | 31.5188 | 13.6791 | 4.9015 | 2.8267 | 0.10745 | 13.5717 | 31.2712 | 9.5315 | 446.125 | 32.2922 | 14.0148 | 4.9613 | 2.8611 | 0.11008 | 13.9047 | 32.0385
500 | 29.5 | 12.803 |  |  | 5.5605 | 3.2066 | 0.13828 | 12.6647 | 29.1814 | 0.21 | 12.593 | 29.0161 | 550 | 6.1165 | 3.5273 | 0.02 | 0.06 | 0.15 | 0.28828 | 12.5147 | 28.8358 | 512.5 | 30.9934 | 13.4512 | 5.6995 | 3.2868 | 0.14528 | 13.3059 | 30.6587 | 9.3448 | 518.75 | 31.754 | 13.7812 | 5.769 | 3.3269 | 0.14884 | 13.6324 | 31.411
Target Velocity | 4 | fps (for 200g salmon transfer)
H | head measured at discharge 8"
dP | Pressure change due to velocity change
g | 32.2 | ft/sec2
density | 62.4 | lb/ft3 |  |  |  | N1 | N2 | Ratio
[6 empty] | 400 | 415 | 0.96386
| H1 | Q1 |  |  |  | Q2 | H2
| 31 | 300 |  |  |  | 311.25 | 33.3686
| 30.2 | 400 |  |  |  | 415 | 32.5075
| 30 | 430 |  |  |  | 446.125 | 32.2922
| 29.5 | 500 |  |  |  | 518.75 | 31.754