## Sheet1
| d1 | 7.98
| d2 | 6.06
8" inlet and outlet N=400 |  | P1 | 6" flow vel. | pressure drop (6" pipe 34 ft Length) |  |  | pressure drop in reducer | 8" inlet and outlet using affinity law N=430 |  | P1 | 6" flow vel. | 8" flow vel | pressure change due to velocity change |  |  | 6" flow vel. | pressure drop (6" pipe 34 ft Length) |  |  | 8" inlet and outlet using affinity law N=440 |  | P1 | 6" flow vel. | pressure drop (6" pipe 34 ft Length) |  |  | pressure change due to velocity change |  |  | 6" flow vel. | 8" flow vel
q (gpm) | H (ft) | H (in PSI) | ft/sec |  | P2 | H new | Dp | q (gpm) | H (ft) | H (in PSI) | ft/sec | ft/sec | dp | P2 | H (new) | ft/sec |  | P2 | H new | q (gpm) | H (ft) | H (in PSI) | ft/sec |  | P2 | H new | dp | P2 | H (new) | ft/sec | ft/sec
|  |  |  | dp | psi | ft | psi |  |  |  | V2 | V1 | psi | Psi | ft |  | dp | psi | ft |  |  |  |  | dp | psi | ft | psi | Psi | ft | V2 | V1
300 | 31 | 13.454 | 3.3363 | 0.26 | 13.194 | 30.4009 | 0.01 | 322.5 | 35.8244 | 15.5478 | 3.5865 | 2.0683 | 0.057527 | 15.4903 | 35.6918 | 3.5865 | 0.31 | 15.2378 | 35.1101 | 330 | 37.51 | 16.2793 | 3.6699 | 0.32 | 15.9593 | 36.7727 | 0.04978 | 13.4042 | 30.8853 | 3.3363 | 1.924
400 | 30.2 | 13.1068 | 4.4484 | 0.46 | 12.6468 | 29.1401 | 0.01 | 430 | 34.8999 | 15.1465 | 4.782 | 2.7577 | 0.10227 | 15.0443 | 34.6642 | 4.782 | 0.54 | 14.6065 | 33.6556 | 440 | 36.542 | 15.8592 | 4.8932 | 0.56 | 15.2992 | 35.2517 | 0.088498 | 13.0183 | 29.9961 | 4.4484 | 2.5653
430 | 30 | 13.02 | 4.782 | 0.53 | 12.49 | 28.7788 | 0.01 | 462.25 | 34.6688 | 15.0462 | 5.1406 | 2.9645 | 0.11819 | 14.9281 | 34.3964 | 5.1406 | 0.61 | 14.4362 | 33.2632 | 473 | 36.3 | 15.7542 | 5.2602 | 0.64 | 15.1142 | 34.8253 | 0.10227 | 12.9177 | 29.7644 | 4.782 | 2.7577
500 | 29.5 | 12.803 | 5.5605 | 0.71 | 12.093 | 27.8641 | 0.02 | 537.5 | 34.0909 | 14.7955 | 5.9775 | 3.4471 | 0.1598 | 14.6357 | 33.7227 | 5.9775 | 0.82 | 13.9755 | 32.2015 | 550 | 35.695 | 15.4916 | 6.1165 | 0.86 | 14.6316 | 33.7134 | 0.13828 | 12.6647 | 29.1814 | 5.5605 | 3.2066
Target Velocity | 4 | fps (for 200g salmon transfer)
H | head measured at discharge 8"
dP | Pressure change
g | 32.2 | ft/sec2
density | 62.4 | lb/ft3
Ratio
0.90909
| N1 | N2
| 400 | 440
| measured values |  | Affinity Law
P1 | H1 | Q1 | Q2 | H2
| 31 | 300 | 330 | 37.51
11.8 | 30.2 | 400 | 440 | 36.542
12.2 | 30 | 430 | 473 | 36.3
12.5 | 29.5 | 500 | 550 | 35.695

## Sheet2
402 | 0.000001217x2 + 0.000481187x - 0.019595242 | 12 | 1.217e-06 | 0.00048118 | 0.019595 | 30 | ft
[6 empty] | 25 | ft
| 556 | 1.2714
| 500 | 1.0818
| 430 | 0.86542
| 400 | 0.77968
| 300 | 0.52417