Pressure loss calculation

Design Input for pressure loss double wall air pipe calculation.

- Fluid 	: air
- Double wall pipe (stainless steel) with outer pipe OD89mm, wall thickness 3mm, inner pipe OD61mm, wall thickness 2mm. the air will blow into the void between inner and outer pipe
- Pipe distance : 7m.
- Number of 90 degree elbows : 7 pcs
- Number of plastic support to inner pipe : 9 pcs
- Air flow capacity 30 m3/h equivalent 0.0083 m3/s.

- Air velocity = 0.0083/0.002529 = 3.3  m/s

- Major loss due to friction calculation.

1A. Hydraulic diameter

dh = 4 (π ro2 - π ri2) / (2 π ro + 2 π ri)

= 2 (ro - ri)

= 2 (41-30) = 22 mm

1B. Friction Coefficient   λ

The friction coefficient - λ - can be calculated by the Colebrooke Equation:

1 / λ1/2 = -2,0 log10 [ (2,51 / (Re λ1/2)) + (k / dh) / 3,72 ]

where

Re = Reynolds number

v = velocity  (m/s)

ρ = density of air (kg/m3)

k / dh = the relative roughness - or roughness ratio

### Reynolds Number for a Pipe or Duct

For a pipe or duct the characteristic length is the hydraulic diameter.

L = dh

where

dh = hydraulic diameter (m, ft)

μ = dynamic or absolute viscosity (Ns/m2) (calc. at 0 deg C)

The Reynolds Number for a duct or pipe can be expressed as

Re = ρ v dh / μ

Re = (3.3 m/s) (0.022 m2 ) (1.23 kg/m3) / (1.79 10-5 Ns/m2)

Re = 4988.7

Turbulent flow indicates that Colebrooks equation (9) must be used to determine the friction coefficient - λ -.

With roughness - ε - for stainless steel 0.0015 mm, the roughness ratio can be calculated:

Roughness Ratio ε = k / dh

= (0.0015 mm) / (22mm)

= 0.00006818

Using the graphical representation of the Colebrooks equation - the Moody Diagram – or refer to (http://www.advdelphisys.com/michael_maley/moody_chart/) the friction coefficient - λ - can be determined to:

λ = 0.0375

The major loss for the 7 m pipe can be calculated with the Darcy-Weisbach Equation (3) or (6):

ploss = λ ( l / dh ) ( ρ v2 / 2 )

= 0.0375 ((7 m) / (0.022 m)) ( (1.23 kg/m3) (3.3 m/s)2 / 2 )

= 79.9 Pa

- Minor loss due to change of velocity in bends.

pminor_loss = ξ (1/2) ρ v2                                       (1)

Loss coefficient elbow’ ξ  usually more and less 0.2 for regular 90 degree 1,5D.

Delta P = 1.5x0.5x1.23x3.32=10 Pa

Hi Chestermiller , can you please advise as following:

- My calculation to major loss due to friction calculation is correct or not?

- My calculation to minor loss due to change of velocity in bends is correct or not?

- The pressure loss to inner pipe support ring is quite difficult as I really have no idea how to calc. because the shape of the air hole is odd. Can you please provide your thoughts?